## YTD Metrics report
Unit | Month | Period Hours | Gross Maximum Capacity MW | MWH | Service Hours | Reserve Shutdown Hours | Available Hours | Available MWH | Forced Outage Hours | Planned Outage Hours | Extended Scheduled Outage Hours | Maintenance Outage Hours | Unavailable Hours | Unplanned Outage Hours | Service Factor | Forced Outage Factor | Availability Factor | Gross Capacity Factor | Equivalent Forced Outage Rate | Unplanned Outage Factor | Number of Reserve Shutdowns | Number of Forced Outages | Number of Planned Outages | Number of Planned Outage Extensions |  | Number of Maintenance Outages | Number of Maintenance Outage Extensions
|  | PH | GMC |  | SH | RSH | AH |  | FOH | POH | ESOH | MOH | UH | UOH | SF | FOF | AF | GCF | EFOR | UOF |  |  |  | Hours | Count |  | Hours | Count
P01 | 2025-01-01 | 744 | 95 | 17256.6 | 182.02 | 0 | 182.02 | 17291.9 | 0 | 561.98 | 0 | 0 | 561.98 | 0 | 24.47 | 0 | 24.47 | 24.42 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P01 | 2025-02-02 | 672 | 95 | 41702.4 | 568.62 | 103.38 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 84.62 | 0 | 100 | 65.32 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2025-03-06 | 744 | 95 | 52947.3 | 712.35 | 29.95 | 742.3 | 70518.5 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 95.75 | 0 | 99.77 | 74.91 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P01 | 2025-04-07 | 720 | 95 | 54653.3 | 698.08 | 21.92 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 96.96 | 0 | 100 | 79.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2025-05-09 | 744 | 95 | 55330.3 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2025-06-10 | 720 | 95 | 53377.2 | 720 | 0 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2025-07-12 | 744 | 95 | 55346.7 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2025-08-13 | 744 | 95 | 41938.7 | 554.43 | 189.57 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 74.52 | 0 | 100 | 59.34 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2025-09-14 | 720 | 95 | 25111.6 | 340.66 | 233.47 | 574.13 | 54542.35 | 0 | 145.87 | 0 | 0 | 145.87 | 0 | 47.31 | 0 | 79.74 | 36.71 | 0 | 0 | 21 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P01 | 2025-10-16 | 744 | 95 | 33078.5 | 424.69 | 246.53 | 671.22 | 63765.9 | 0 | 72.78 | 0 | 0 | 72.78 | 0 | 57.08 | 0 | 90.22 | 46.8 | 0 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P01 | 2025-11-17 | 720 | 95 | 36101 | 470.4 | 242.92 | 713.32 | 67765.4 | 0 | 6.68 | 0 | 0 | 6.68 | 0 | 65.33 | 0 | 99.07 | 52.78 | 0 | 0 | 34 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P01 | 2024-12-19 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P01 | Total | 8760 | 95 | 466843.6 | 6159.25 | 1067.74 | 7226.99 | 686564.05 | 0 | 1533.01 | 0 | 0 | 1533.01 | 0 | 70.5033 | 0 | 82.7725 | 56.2342 | 0 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0
P02 | 2025-01-01 | 744 | 95 | 47153.2 | 649.01 | 92.17 | 741.18 | 70412.1 | 0 | 2.82 | 0 | 0 | 2.82 | 0 | 87.23 | 0 | 99.62 | 66.71 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P02 | 2025-02-02 | 672 | 95 | 28352.7 | 392.18 | 269.57 | 661.75 | 62866.25 | 0 | 0 | 0.25 | 10 | 10.25 | 10 | 58.36 | 0 | 98.47 | 44.41 | 0 | 0.014881 | 10 | 0 | 0 | 0 | 0 | 1 | 0.25 | 1
P02 | 2025-03-06 | 744 | 95 | 32670.8 | 447.43 | 295.3 | 742.73 | 70559.35 | 0 | 1.27 | 0 | 0 | 1.27 | 0 | 60.14 | 0 | 99.83 | 46.22 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P02 | 2025-04-07 | 720 | 95 | 54504.4 | 696.95 | 23.05 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8 | 0 | 100 | 79.68 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2025-05-09 | 744 | 95 | 55200 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2025-06-10 | 720 | 95 | 53017.6 | 716.93 | 3.07 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 99.57 | 0 | 100 | 77.51 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2025-07-12 | 744 | 95 | 55239.1 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2025-08-13 | 744 | 95 | 40975.3 | 541.7 | 202.3 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 72.81 | 0 | 100 | 57.97 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2025-09-14 | 720 | 95 | 20271.2 | 277.02 | 296.9 | 573.92 | 54522.4 | 0 | 146.08 | 0 | 0 | 146.08 | 0 | 38.48 | 0 | 79.71 | 29.64 | 0 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P02 | 2025-10-16 | 744 | 95 | 32918 | 423.03 | 236.1 | 659.13 | 62617.35 | 0 | 84.87 | 0 | 0 | 84.87 | 0 | 56.86 | 0 | 88.59 | 46.57 | 0 | 0 | 24 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P02 | 2025-11-17 | 720 | 95 | 37453.1 | 492.15 | 221.17 | 713.32 | 67765.4 | 0 | 6.68 | 0 | 0 | 6.68 | 0 | 68.35 | 0 | 99.07 | 54.76 | 0 | 0 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P02 | 2024-12-19 | 744 | 95 | 53589.9 | 726.98 | 15.95 | 742.93 | 70578.35 | 1.07 | 0 | 0 | 0 | 1.07 | 1.07 | 97.71 | 0.14 | 99.86 | 75.82 | 0.15 | 0.0014382 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P02 | Total | 8760 | 95 | 511345.3 | 6851.38 | 1655.58 | 8506.96 | 808161.2 | 1.07 | 241.72 | 0.25 | 10 | 253.04 | 11.07 | 78.0258 | 0.011667 | 97.0958 | 61.295 | 0.0125 | 0.0013599 | 126 | 1 | 7 | 0 | 0 | 1 | 0.25 | 1
P03 | 2025-01-01 | 744 | 95 | 37058.8 | 531.47 | 212.53 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 71.43 | 0 | 100 | 52.43 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-02-02 | 672 | 95 | 46356 | 651.27 | 20.73 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 96.92 | 0 | 100 | 72.61 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-03-06 | 744 | 95 | 53457.6 | 734.77 | 7.8 | 742.57 | 70544.15 | 0 | 1.43 | 0 | 0 | 1.43 | 0 | 98.76 | 0 | 99.81 | 75.63 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P03 | 2025-04-07 | 720 | 95 | 54651.3 | 706.05 | 13.95 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 98.06 | 0 | 100 | 79.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-05-09 | 744 | 95 | 54517.1 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 77.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-06-10 | 720 | 95 | 50729.4 | 697.13 | 22.87 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 96.82 | 0 | 100 | 74.17 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-07-12 | 744 | 95 | 52681.1 | 722.68 | 21.32 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 97.13 | 0 | 100 | 74.53 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-08-13 | 744 | 95 | 47072.3 | 637.9 | 106.1 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 85.74 | 0 | 100 | 66.6 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2025-09-14 | 720 | 95 | 36751.4 | 550.58 | 120.75 | 671.33 | 63776.35 | 0 | 48.67 | 0 | 0 | 48.67 | 0 | 76.47 | 0 | 93.24 | 53.73 | 0 | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P03 | 2025-10-16 | 744 | 95 | 34318 | 470.97 | 127.15 | 598.12 | 56821.4 | 0 | 145.88 | 0 | 0 | 145.88 | 0 | 63.3 | 0 | 80.39 | 48.55 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P03 | 2025-11-17 | 720 | 95 | 42293.3 | 564.42 | 137.52 | 701.94 | 66684.3 | 0 | 4.83 | 3.78 | 9.45 | 18.06 | 9.45 | 78.39 | 0 | 97.49 | 61.83 | 0 | 0.013125 | 17 | 0 | 1 | 3.78 | 1 | 1 | 0 | 0
P03 | 2024-12-19 | 744 | 95 | 42954.5 | 593.27 | 149.83 | 743.1 | 70594.5 | 0.9 | 0 | 0 | 0 | 0.9 | 0.9 | 79.74 | 0.12 | 99.88 | 60.77 | 0.15 | 0.0012097 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P03 | Total | 8760 | 95 | 552840.8 | 7604.51 | 940.55 | 8545.06 | 811780.7 | 0.9 | 200.81 | 3.78 | 9.45 | 214.94 | 10.35 | 86.8967 | 0.01 | 97.5675 | 66.49 | 0.0125 | 0.0011946 | 116 | 1 | 6 | 3.78 | 1 | 1 | 0 | 0
P04 | 2025-01-01 | 744 | 95 | 43294 | 594.76 | 141.37 | 736.13 | 69932.35 | 0 | 0 | 0 | 7.87 | 7.87 | 7.87 | 79.94 | 0 | 98.94 | 61.25 | 0 | 0.010578 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P04 | 2025-02-02 | 672 | 95 | 23378.9 | 324.9 | 347.1 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 48.35 | 0 | 100 | 36.62 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2025-03-06 | 744 | 95 | 13188.6 | 168.63 | 575.37 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 22.67 | 0 | 100 | 18.66 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2025-04-07 | 720 | 95 | 54174.4 | 694.16 | 24.12 | 718.28 | 68236.6 | 0 | 1.72 | 0 | 0 | 1.72 | 0 | 96.41 | 0 | 99.76 | 79.2 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P04 | 2025-05-09 | 744 | 95 | 55174.4 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2025-06-10 | 720 | 95 | 52009.8 | 704.15 | 15.85 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8 | 0 | 100 | 76.04 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2025-07-12 | 744 | 95 | 47017.9 | 639.1 | 104.9 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9 | 0 | 100 | 66.52 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2025-08-13 | 744 | 95 | 44949.8 | 603.55 | 140.45 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 81.12 | 0 | 100 | 63.6 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2025-09-14 | 720 | 95 | 16395.9 | 219.66 | 451.67 | 671.33 | 63776.35 | 0 | 48.67 | 0 | 0 | 48.67 | 0 | 30.51 | 0 | 93.24 | 23.97 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P04 | 2025-10-16 | 744 | 95 | 22013 | 287.1 | 308 | 595.1 | 56534.5 | 0 | 148.9 | 0 | 0 | 148.9 | 0 | 38.59 | 0 | 79.99 | 31.14 | 0 | 0 | 27 | 0 | 3 | 0 | 0 | 0 | 0 | 0
P04 | 2025-11-17 | 720 | 95 | 35813.3 | 466.62 | 237.43 | 704.05 | 66884.75 | 0 | 12.17 | 3.78 | 0 | 15.95 | 0 | 64.81 | 0 | 97.78 | 52.36 | 0 | 0 | 24 | 0 | 2 | 3.78 | 1 | 0 | 0 | 0
P04 | 2024-12-19 | 744 | 95 | 31683.8 | 438 | 68.38 | 506.38 | 48106.1 | 1.07 | 236.55 | 0 | 0 | 237.62 | 1.07 | 58.87 | 0.14 | 68.06 | 44.83 | 0.24 | 0.0014382 | 11 | 1 | 2 | 0 | 0 | 0 | 0 | 0
P04 | Total | 8760 | 95 | 439093.8 | 5884.63 | 2414.64 | 8299.27 | 788430.65 | 1.07 | 448.01 | 3.78 | 7.87 | 460.73 | 8.94 | 67.0808 | 0.011667 | 94.8142 | 52.6875 | 0.02 | 0.0010013 | 175 | 1 | 10 | 3.78 | 1 | 1 | 0 | 0
P05 | 2025-01-01 | 744 | 95 | 37260 | 527.9 | 102.32 | 630.22 | 59870.9 | 0 | 113.78 | 0 | 0 | 113.78 | 0 | 70.95 | 0 | 84.71 | 52.72 | 0 | 0 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-02-02 | 672 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 672 | 0 | 0 | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-03-06 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-04-07 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-05-09 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-06-10 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-07-12 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-08-13 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-09-14 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-10-16 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2025-11-17 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2024-12-19 | 744 | 95 | 49428.9 | 688.1 | 55.9 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 92.49 | 0 | 100 | 69.93 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | Total | 8760 | 95 | 86688.9 | 1216 | 158.22 | 1374.22 | 130550.9 | 0 | 7385.78 | 0 | 0 | 7385.78 | 0 | 13.62 | 0 | 15.3925 | 10.2208 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 0 | 0 | 0
P06 | 2025-01-01 | 744 | 95 | 47666 | 679.16 | 59.07 | 738.23 | 70131.85 | 0 | 5.77 | 0 | 0 | 5.77 | 0 | 91.28 | 0 | 99.22 | 67.44 | 0 | 0 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P06 | 2025-02-02 | 672 | 95 | 37216 | 529.83 | 142.17 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 78.84 | 0 | 100 | 58.3 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2025-03-06 | 744 | 95 | 15537 | 215.64 | 520.38 | 736.02 | 69921.9 | 0 | 7.98 | 0 | 0 | 7.98 | 0 | 28.98 | 0 | 98.93 | 21.98 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P06 | 2025-04-07 | 720 | 95 | 51658 | 663.72 | 54.48 | 718.2 | 68229 | 0 | 1.8 | 0 | 0 | 1.8 | 0 | 92.18 | 0 | 99.75 | 75.52 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P06 | 2025-05-09 | 744 | 95 | 48664 | 662.23 | 79.67 | 741.9 | 70480.5 | 2.1 | 0 | 0 | 0 | 2.1 | 2.1 | 89.01 | 0.28 | 99.72 | 68.85 | 0.32 | 0.0028226 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2025-06-10 | 720 | 95 | 46635 | 642.25 | 77.75 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2 | 0 | 100 | 68.18 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2025-07-12 | 744 | 95 | 35792 | 499 | 245 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 67.07 | 0 | 100 | 50.64 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2025-08-13 | 744 | 95 | 53837 | 737.25 | 6.75 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 99.09 | 0 | 100 | 76.17 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2025-09-14 | 720 | 95 | 48709 | 714.05 | 0.83 | 714.88 | 67913.6 | 0 | 0 | 0.12 | 5 | 5.12 | 5 | 99.17 | 0 | 99.29 | 71.21 | 0 | 0.0069444 | 2 | 0 | 0 | 0 | 0 | 1 | 0.12 | 1
P06 | 2025-10-16 | 744 | 95 | 55550 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 78.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2025-11-17 | 720 | 95 | 51756 | 686.73 | 33.27 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 95.38 | 0 | 100 | 75.67 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2024-12-19 | 744 | 95 | 51942.7 | 723.73 | 20.27 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 97.28 | 0 | 100 | 73.49 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | Total | 8760 | 95 | 544962.7 | 7497.59 | 1239.64 | 8737.23 | 830036.85 | 2.1 | 15.55 | 0.12 | 5 | 22.77 | 7.1 | 85.6233 | 0.023333 | 99.7425 | 65.5033 | 0.026667 | 0.00081392 | 97 | 1 | 3 | 0 | 0 | 1 | 0.12 | 1
P07 | 2025-01-01 | 744 | 95 | 43262.7 | 592.55 | 151.45 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 79.64 | 0 | 100 | 61.21 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P07 | 2025-02-02 | 672 | 95 | 33026.4 | 444.33 | 227.67 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 66.12 | 0 | 100 | 51.73 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P07 | 2025-03-06 | 744 | 95 | 51355.6 | 691.08 | 40.25 | 731.33 | 69476.35 | 0 | 8.67 | 0 | 4 | 12.67 | 4 | 92.89 | 0 | 98.3 | 72.66 | 0 | 0.0053763 | 6 | 0 | 1 | 0 | 0 | 1 | 0 | 0
P07 | 2025-04-07 | 720 | 95 | 53142.8 | 676.67 | 41.93 | 718.6 | 68267 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 93.98 | 0 | 99.81 | 77.69 | 0 | 0 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2025-05-09 | 744 | 95 | 48043.1 | 644.83 | 89.5 | 734.33 | 69761.35 | 2.1 | 7.57 | 0 | 0 | 9.67 | 2.1 | 86.67 | 0.28 | 98.7 | 67.97 | 0.32 | 0.0028226 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2025-06-10 | 720 | 95 | 43195.2 | 587.12 | 132.88 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 81.54 | 0 | 100 | 63.15 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P07 | 2025-07-12 | 744 | 95 | 25491 | 349.92 | 394.08 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 47.03 | 0 | 100 | 36.07 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P07 | 2025-08-13 | 744 | 95 | 39261.8 | 519.72 | 220.53 | 740.25 | 70323.75 | 0 | 0 | 0 | 3.75 | 3.75 | 3.75 | 69.85 | 0 | 99.5 | 55.55 | 0 | 0.0050403 | 27 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P07 | 2025-09-14 | 720 | 95 | 10662 | 150.22 | 191.78 | 342 | 32490 | 0 | 378 | 0 | 0 | 378 | 0 | 20.86 | 0 | 47.5 | 15.59 | 0 | 0 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2025-10-16 | 744 | 95 | 5963.5 | 77.53 | 3.62 | 81.15 | 7709.25 | 0 | 662.85 | 0 | 0 | 662.85 | 0 | 10.42 | 0 | 10.91 | 8.44 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2025-11-17 | 720 | 95 | 36709.8 | 475.78 | 235.5 | 711.28 | 67571.6 | 0 | 8.72 | 0 | 0 | 8.72 | 0 | 66.08 | 0 | 98.79 | 53.67 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P07 | 2024-12-19 | 744 | 95 | 46834.7 | 632.32 | 111.68 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 84.99 | 0 | 100 | 66.26 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P07 | Total | 8760 | 95 | 436948.6 | 5842.07 | 1840.87 | 7682.94 | 729879.3 | 2.1 | 1067.21 | 0 | 7.75 | 1077.06 | 9.85 | 66.6725 | 0.023333 | 87.7925 | 52.4992 | 0.026667 | 0.0011033 | 207 | 1 | 7 | 0 | 0 | 2 | 0 | 0
P08 | 2025-01-01 | 744 | 95 | 38338.7 | 523.47 | 217.2 | 740.67 | 70363.65 | 0 | 3.33 | 0 | 0 | 3.33 | 0 | 70.36 | 0 | 99.55 | 54.24 | 0 | 0 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2025-02-02 | 672 | 95 | 29238.7 | 401.87 | 270.13 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 59.8 | 0 | 100 | 45.8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2025-03-06 | 744 | 95 | 3961.4 | 52.27 | 1.75 | 54.02 | 5131.9 | 0 | 689.98 | 0 | 0 | 689.98 | 0 | 7.03 | 0 | 7.26 | 5.6 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2025-04-07 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2025-05-09 | 744 | 95 | 16114 | 220.75 | 3.82 | 224.57 | 21334.15 | 0 | 519.43 | 0 | 0 | 519.43 | 0 | 29.67 | 0 | 30.18 | 22.8 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2025-06-10 | 720 | 95 | 30686.2 | 412.1 | 285.1 | 697.2 | 66234 | 17.82 | 0 | 0 | 4.98 | 22.8 | 22.8 | 57.24 | 2.48 | 96.83 | 44.86 | 4.14 | 0.031667 | 31 | 1 | 0 | 0 | 0 | 1 | 0 | 0
P08 | 2025-07-12 | 744 | 95 | 15647.7 | 216.03 | 527.97 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 29.04 | 0 | 100 | 22.14 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2025-08-13 | 744 | 95 | 37387.3 | 497.07 | 246.93 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 66.81 | 0 | 100 | 52.9 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2025-09-14 | 720 | 95 | 17403 | 228.52 | 386.03 | 614.55 | 58382.25 | 0 | 105.45 | 0 | 0 | 105.45 | 0 | 31.74 | 0 | 85.35 | 25.44 | 0 | 0 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2025-10-16 | 744 | 95 | 35388.3 | 454.62 | 159.38 | 614 | 58330 | 0 | 0 | 0 | 130 | 130 | 130 | 61.1 | 0 | 82.53 | 50.07 | 0 | 0.17473 | 21 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P08 | 2025-11-17 | 720 | 95 | 33317.4 | 433.48 | 278.37 | 711.85 | 67625.75 | 0 | 8.15 | 0 | 0 | 8.15 | 0 | 60.21 | 0 | 98.87 | 48.71 | 0 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P08 | 2024-12-19 | 744 | 95 | 44158.7 | 595.3 | 148.7 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 80.01 | 0 | 100 | 62.48 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | Total | 8760 | 95 | 301641.4 | 4035.48 | 2525.38 | 6560.86 | 623281.7 | 17.82 | 2046.34 | 0 | 134.98 | 2199.14 | 152.8 | 46.0842 | 0.20667 | 75.0475 | 36.2533 | 0.345 | 0.0172 | 225 | 1 | 7 | 0 | 0 | 2 | 0 | 0
P09 | 2025-01-01 | 744 | 95 | 33418.8 | 459.25 | 284.75 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 61.73 | 0 | 100 | 47.28 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-02-02 | 672 | 95 | 10320.9 | 139.85 | 528.83 | 668.68 | 63524.6 | 3.32 | 0 | 0 | 0 | 3.32 | 3.32 | 20.81 | 0.49 | 99.51 | 16.17 | 2.32 | 0.0049405 | 14 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-03-06 | 744 | 95 | 27508 | 375.02 | 368.98 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 50.41 | 0 | 100 | 38.92 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-04-07 | 720 | 95 | 46024.2 | 593.32 | 125.43 | 718.75 | 68281.25 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 82.41 | 0 | 99.83 | 67.29 | 0 | 0 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P09 | 2025-05-09 | 744 | 95 | 35225.3 | 478.93 | 265.07 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 64.37 | 0 | 100 | 49.84 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-06-10 | 720 | 95 | 26556.3 | 365.68 | 354.32 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 50.79 | 0 | 100 | 38.82 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-07-12 | 744 | 95 | 2584 | 37.2 | 706.8 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 100 | 3.66 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-08-13 | 744 | 95 | 34217.2 | 457.05 | 286.95 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 61.43 | 0 | 100 | 48.41 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-09-14 | 720 | 95 | 26380.5 | 349.87 | 370.13 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 48.59 | 0 | 100 | 38.57 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2025-10-16 | 744 | 95 | 22085.6 | 276.2 | 360.25 | 636.45 | 60462.75 | 0 | 107.55 | 0 | 0 | 107.55 | 0 | 37.12 | 0 | 85.54 | 31.25 | 0 | 0 | 25 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P09 | 2025-11-17 | 720 | 95 | 30510.1 | 391.37 | 328.63 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 54.36 | 0 | 100 | 44.61 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2024-12-19 | 744 | 95 | 44643.5 | 607.63 | 131.42 | 739.05 | 70209.75 | 0 | 4.95 | 0 | 0 | 4.95 | 0 | 81.67 | 0 | 99.33 | 63.16 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P09 | Total | 8760 | 95 | 339474.4 | 4531.37 | 4111.56 | 8642.93 | 821078.35 | 3.32 | 113.75 | 0 | 0 | 117.07 | 3.32 | 51.5575 | 0.040833 | 98.6842 | 40.665 | 0.19333 | 0.00041171 | 216 | 25 | 3 | 1 | 0 | 0 | 0 | 0
P10 | 2025-01-01 | 744 | 95 | 46988.4 | 669.3 | 74.7 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 89.96 | 0 | 100 | 66.48 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-02-02 | 672 | 95 | 46374.7 | 650.83 | 21.17 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 96.85 | 0 | 100 | 72.64 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-03-06 | 744 | 95 | 54270.1 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 76.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-04-07 | 720 | 95 | 10189 | 134.99 | 12.97 | 147.96 | 14056.2 | 570.57 | 1.47 | 0 | 0 | 572.04 | 570.57 | 18.75 | 79.25 | 20.55 | 14.9 | 80.87 | 0.79246 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0
P10 | 2025-05-09 | 744 | 95 | 20899.6 | 283.68 | 425.67 | 709.35 | 67388.25 | 34.65 | 0 | 0 | 0 | 34.65 | 34.65 | 38.13 | 4.66 | 95.34 | 29.57 | 10.88 | 0.046573 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-06-10 | 720 | 95 | 10032.1 | 140.03 | 579.97 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 19.45 | 0 | 100 | 14.67 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-07-12 | 744 | 95 | 79.4 | 1.43 | 742.57 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 100 | 0.11 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-08-13 | 744 | 95 | 46517.7 | 632.18 | 92.7 | 724.88 | 68863.6 | 19.12 | 0 | 0 | 0 | 19.12 | 19.12 | 84.97 | 2.57 | 97.43 | 65.81 | 2.94 | 0.025699 | 19 | 3 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-09-14 | 720 | 95 | 40383.6 | 597.35 | 122.65 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 82.97 | 0 | 100 | 59.04 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2025-10-16 | 744 | 95 | 40044.4 | 536.94 | 105.28 | 642.22 | 61010.9 | 20.33 | 81.45 | 0 | 0 | 101.78 | 20.33 | 72.17 | 2.73 | 86.32 | 56.66 | 3.65 | 0.027325 | 15 | 1 | 1 | 0 | 0 | 0 | 0 | 0
P10 | 2025-11-17 | 720 | 95 | 47071.6 | 627.23 | 92.77 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 87.12 | 0 | 100 | 68.82 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2024-12-19 | 744 | 95 | 47892.2 | 666.68 | 72.37 | 739.05 | 70209.75 | 0 | 4.95 | 0 | 0 | 4.95 | 0 | 89.61 | 0 | 99.33 | 67.76 | 0 | 0 | 0 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P10 | Total | 8760 | 95 | 410742.8 | 5684.64 | 2342.82 | 8027.46 | 762608.7 | 644.67 | 87.87 | 0 | 0 | 732.54 | 644.67 | 65.0142 | 7.4342 | 91.5808 | 49.4367 | 8.195 | 0.074338 | 92 | 15 | 2 | 1 | 0 | 0 | 0 | 0
PR | TOTAL | 87600 |  | 4090582.3 | 55306.92 | 18297 | 73603.92 | 6992372.4 | 673.05 | 13140.05 | 7.93 | 175.05 | 13996.08 | 848.1 | 63.1078 | 0.77617 | 84.049 | 49.1285 | 0.88317 | 0.0097422 | 1388 | 46 | 64 | 9.56 | 2 | 8 | 0.37 | 2
W01 | 2025-01-01 | 744 | 122 | 38919.1 | 536.47 | 207.53 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 72.11 | 0 | 100 | 42.88 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-02-02 | 672 | 122 | 28886.9 | 413.42 | 258.58 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 61.52 | 0 | 100 | 35.23 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-03-06 | 744 | 122 | 31983.7 | 448.02 | 294.35 | 742.37 | 90569.14 | 0 | 0 | 0 | 1.63 | 1.63 | 1.63 | 60.22 | 0 | 99.78 | 38.54 | 0 | 0.0021909 | 41 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W01 | 2025-04-07 | 720 | 122 | 29337.8 | 392.05 | 314.82 | 706.87 | 86238.14 | 0 | 0 | 0 | 13.13 | 13.13 | 13.13 | 54.45 | 0 | 98.18 | 33.4 | 0 | 0.018236 | 37 | 0 | 0 | 0 | 0 | 2 | 0 | 0
W01 | 2025-05-09 | 744 | 122 | 26571.8 | 350.82 | 393.18 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 47.15 | 0 | 100 | 29.27 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-06-10 | 720 | 122 | 12303.9 | 173.38 | 546.62 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 24.08 | 0 | 100 | 14.01 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-07-12 | 744 | 122 | 1682.3 | 24.65 | 719.35 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 0 | 100 | 1.85 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-08-13 | 744 | 122 | 44528.8 | 604.82 | 139.18 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 81.29 | 0 | 100 | 49.06 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-09-14 | 720 | 122 | 45724 | 635.45 | 84.55 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 88.26 | 0 | 100 | 52.05 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2025-10-16 | 744 | 122 | 49708 | 682.25 | 30.72 | 712.97 | 86982.34 | 0 | 31.03 | 0 | 0 | 31.03 | 0 | 91.7 | 0 | 95.83 | 54.76 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W01 | 2025-11-17 | 720 | 122 | 49718.8 | 680.42 | 39.58 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5 | 0 | 100 | 56.6 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2024-12-19 | 744 | 122 | 20644.9 | 280.05 | 69.8 | 349.85 | 42681.7 | 0 | 112 | 282.15 | 0 | 394.15 | 0 | 37.64 | 0 | 47.02 | 22.74 | 0 | 0 | 17 | 0 | 1 | 282.15 | 1 | 0 | 0 | 0
W01 | Total | 8760 | 122 | 380010 | 5221.8 | 3098.26 | 8320.06 | 1015047.32 | 0 | 143.03 | 282.15 | 14.76 | 439.94 | 14.76 | 59.6858 | 0 | 95.0675 | 35.8658 | 0 | 0.0017022 | 267 | 0 | 2 | 282.15 | 1 | 3 | 0 | 0
W02 | 2025-01-01 | 744 | 122 | 53107.4 | 741.72 | 2.28 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.69 | 0 | 100 | 58.51 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-02-02 | 672 | 122 | 46725 | 668.85 | 3.15 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 99.53 | 0 | 100 | 56.99 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-03-06 | 744 | 122 | 52327.8 | 743.82 | 0.18 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.98 | 0 | 100 | 57.65 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-04-07 | 720 | 122 | 37993.2 | 507.09 | 199.78 | 706.87 | 86238.14 | 0 | 0 | 0 | 13.13 | 13.13 | 13.13 | 70.43 | 0 | 98.18 | 43.25 | 0 | 0.018236 | 32 | 0 | 0 | 0 | 0 | 2 | 0 | 0
W02 | 2025-05-09 | 744 | 122 | 34691.8 | 459.93 | 284.07 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 61.82 | 0 | 100 | 38.22 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-06-10 | 720 | 122 | 22497.8 | 313.87 | 406.13 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 43.59 | 0 | 100 | 25.61 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-07-12 | 744 | 122 | 5407.6 | 78.17 | 665.83 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 10.51 | 0 | 100 | 5.96 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-08-13 | 744 | 122 | 54127.1 | 730.35 | 13.65 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 98.17 | 0 | 100 | 59.63 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-09-14 | 720 | 122 | 21503.3 | 299.75 | 420.25 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 41.63 | 0 | 100 | 24.48 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2025-10-16 | 744 | 122 | 20793.1 | 283.72 | 429.25 | 712.97 | 86982.34 | 0 | 31.03 | 0 | 0 | 31.03 | 0 | 38.13 | 0 | 95.83 | 22.91 | 0 | 0 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W02 | 2025-11-17 | 720 | 122 | 42921.3 | 585.42 | 133.73 | 719.15 | 87736.3 | 0.85 | 0 | 0 | 0 | 0.85 | 0.85 | 81.31 | 0.12 | 99.88 | 48.86 | 0.14 | 0.0011806 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2024-12-19 | 744 | 122 | 53468.7 | 720.52 | 23.48 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 96.84 | 0 | 100 | 58.91 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | Total | 8760 | 122 | 445564.1 | 6133.21 | 2581.78 | 8714.99 | 1063228.78 | 0.85 | 31.03 | 0 | 13.13 | 45.01 | 13.98 | 70.1358 | 0.01 | 99.4908 | 41.7483 | 0.011667 | 0.0016181 | 208 | 1 | 1 | 0 | 0 | 2 | 0 | 0
W03 | 2025-01-01 | 744 | 122 | 47799.3 | 666.65 | 77.35 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 100 | 52.66 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-02-02 | 672 | 122 | 39734.6 | 569.47 | 102.53 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 84.74 | 0 | 100 | 48.47 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-03-06 | 744 | 122 | 39936.8 | 570.35 | 173.65 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 76.66 | 0 | 100 | 44 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-04-07 | 720 | 122 | 41185.6 | 550.07 | 167.5 | 717.57 | 87543.54 | 0 | 2.43 | 0 | 0 | 2.43 | 0 | 76.4 | 0 | 99.66 | 46.89 | 0 | 0 | 35 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W03 | 2025-05-09 | 744 | 122 | 44493 | 590.7 | 153.3 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4 | 0 | 100 | 49.02 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-06-10 | 720 | 122 | 33136.7 | 459.85 | 260.15 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 63.87 | 0 | 100 | 37.72 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-07-12 | 744 | 122 | 14991.5 | 211.23 | 532.77 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 28.39 | 0 | 100 | 16.52 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-08-13 | 744 | 122 | 49327.6 | 665.6 | 78.4 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 89.46 | 0 | 100 | 54.35 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2025-09-14 | 720 | 122 | 38969.7 | 548.65 | 164.08 | 712.73 | 86953.06 | 0 | 7.27 | 0 | 0 | 7.27 | 0 | 76.2 | 0 | 98.99 | 44.36 | 0 | 0 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W03 | 2025-10-16 | 744 | 122 | 44393.9 | 615.66 | 71.25 | 686.91 | 83803.02 | 0 | 9.82 | 0 | 47.27 | 57.09 | 47.27 | 82.75 | 0 | 92.33 | 48.91 | 0 | 0.063535 | 10 | 0 | 1 | 0 | 0 | 1 | 0 | 0
W03 | 2025-11-17 | 720 | 122 | 50372.1 | 686.88 | 33.12 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4 | 0 | 100 | 57.35 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2024-12-19 | 744 | 122 | 49372.3 | 665.15 | 78.85 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4 | 0 | 100 | 54.39 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | Total | 8760 | 122 | 493713.1 | 6800.26 | 1892.95 | 8693.21 | 1060571.62 | 0 | 19.52 | 0 | 47.27 | 66.79 | 47.27 | 77.6892 | 0 | 99.2483 | 46.22 | 0 | 0.0052946 | 265 | 0 | 3 | 0 | 0 | 1 | 0 | 0
W04 | 2025-01-01 | 744 | 122 | 33043.5 | 463.7 | 280.3 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 62.33 | 0 | 100 | 36.4 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-02-02 | 672 | 122 | 12692.5 | 183.28 | 488.72 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 27.27 | 0 | 100 | 15.48 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-03-06 | 744 | 122 | 13537.3 | 187.42 | 556.58 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 25.19 | 0 | 100 | 14.91 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-04-07 | 720 | 122 | 43698.3 | 593.69 | 124.13 | 717.82 | 87574.04 | 0 | 2.18 | 0 | 0 | 2.18 | 0 | 82.46 | 0 | 99.7 | 49.75 | 0 | 0 | 48 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W04 | 2025-05-09 | 744 | 122 | 46880.7 | 635.46 | 74.67 | 710.13 | 86635.86 | 33.87 | 0 | 0 | 0 | 33.87 | 33.87 | 85.41 | 4.55 | 95.45 | 51.65 | 5.06 | 0.045524 | 29 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-06-10 | 720 | 122 | 39399.2 | 554.07 | 165.93 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 76.95 | 0 | 100 | 44.85 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-07-12 | 744 | 122 | 24027.1 | 340.47 | 403.53 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 45.76 | 0 | 100 | 26.47 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-08-13 | 744 | 122 | 22781.9 | 313.3 | 430.7 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 42.11 | 0 | 100 | 25.1 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2025-09-14 | 720 | 122 | 3382.7 | 44.58 | 298.02 | 342.6 | 41797.2 | 0 | 377.4 | 0 | 0 | 377.4 | 0 | 6.19 | 0 | 47.58 | 3.85 | 0 | 0 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W04 | 2025-10-16 | 744 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W04 | 2025-11-17 | 720 | 122 | 17485.6 | 233.8 | 87.37 | 321.17 | 39182.74 | 0 | 328 | 70.83 | 0 | 398.83 | 0 | 32.47 | 0 | 44.61 | 19.91 | 0 | 0 | 9 | 0 | 1 | 70.83 | 1 | 0 | 0 | 0
W04 | 2024-12-19 | 744 | 122 | 35018.7 | 474.85 | 269.15 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 63.82 | 0 | 100 | 38.58 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | Total | 8760 | 122 | 291947.5 | 4024.62 | 3179.1 | 7203.72 | 878853.84 | 33.87 | 1451.58 | 70.83 | 0 | 1556.28 | 33.87 | 45.83 | 0.37917 | 82.2783 | 27.2458 | 0.42167 | 0.0037937 | 271 | 1 | 4 | 70.83 | 1 | 0 | 0 | 0
W05 | 2025-01-01 | 744 | 122 | 19141 | 272 | 462.38 | 734.38 | 89594.36 | 0 | 9.62 | 0 | 0 | 9.62 | 0 | 36.56 | 0 | 98.71 | 21.09 | 0 | 0 | 34 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W05 | 2025-02-02 | 672 | 122 | 7403 | 106.38 | 565.62 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 15.83 | 0 | 100 | 9.03 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2025-03-06 | 744 | 122 | 7248.2 | 99.05 | 640.75 | 739.8 | 90255.6 | 0 | 4 | 0.2 | 0 | 4.2 | 0 | 13.31 | 0 | 99.44 | 7.99 | 0 | 0 | 11 | 0 | 1 | 0.2 | 1 | 0 | 0 | 0
W05 | 2025-04-07 | 720 | 122 | 45466.8 | 620.58 | 95.72 | 716.3 | 87388.6 | 0 | 3.7 | 0 | 0 | 3.7 | 0 | 86.19 | 0 | 99.49 | 51.76 | 0 | 0 | 37 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W05 | 2025-05-09 | 744 | 122 | 51912.4 | 704.45 | 39.55 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 94.68 | 0 | 100 | 57.19 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2025-06-10 | 720 | 122 | 43474.5 | 613.45 | 106.55 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2 | 0 | 100 | 49.49 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2025-07-12 | 744 | 122 | 31784.5 | 449.77 | 294.23 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 60.45 | 0 | 100 | 35.02 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2025-08-13 | 744 | 122 | 10465.3 | 149.65 | 594.35 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 20.11 | 0 | 100 | 11.53 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2025-09-14 | 720 | 122 | 4738.8 | 68.35 | 651.65 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 9.49 | 0 | 100 | 5.4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2025-10-16 | 744 | 122 | 13212.1 | 188.85 | 469.45 | 658.3 | 80312.6 | 0 | 85.7 | 0 | 0 | 85.7 | 0 | 25.38 | 0 | 88.48 | 14.56 | 0 | 0 | 24 | 0 | 2 | 0 | 0 | 0 | 0 | 0
W05 | 2025-11-17 | 720 | 122 | 19429.3 | 259.93 | 457.97 | 717.9 | 87583.8 | 0 | 0 | 0 | 2.1 | 2.1 | 2.1 | 36.1 | 0 | 99.71 | 22.12 | 0 | 0.0029167 | 24 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W05 | 2024-12-19 | 744 | 122 | 26174.5 | 360.22 | 376.48 | 736.7 | 89877.4 | 0 | 0 | 0.43 | 6.87 | 7.3 | 6.87 | 48.42 | 0 | 99.02 | 28.84 | 0 | 0.0092339 | 22 | 0 | 0 | 0 | 0 | 1 | 0.43 | 1
W05 | Total | 8760 | 122 | 280450.4 | 3892.68 | 4754.7 | 8647.38 | 1054980.36 | 0 | 103.02 | 0.63 | 8.97 | 112.62 | 8.97 | 44.31 | 0 | 98.7375 | 26.1683 | 0 | 0.0010125 | 266 | 0 | 5 | 0.2 | 1 | 2 | 0.43 | 1
W06 | 2025-01-01 | 744 | 122 | 43147.8 | 603.55 | 130.83 | 734.38 | 89594.36 | 0 | 9.62 | 0 | 0 | 9.62 | 0 | 81.12 | 0 | 98.71 | 47.54 | 0 | 0 | 28 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W06 | 2025-02-02 | 672 | 122 | 32751.3 | 478.6 | 193.4 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 71.22 | 0 | 100 | 39.95 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2025-03-06 | 744 | 122 | 44450.3 | 637.05 | 102.75 | 739.8 | 90255.6 | 0 | 4 | 0.2 | 0 | 4.2 | 0 | 85.63 | 0 | 99.44 | 48.97 | 0 | 0 | 8 | 0 | 1 | 0.2 | 1 | 0 | 0 | 0
W06 | 2025-04-07 | 720 | 122 | 52077.2 | 706.45 | 11.5 | 717.95 | 87589.9 | 0 | 2.05 | 0 | 0 | 2.05 | 0 | 98.12 | 0 | 99.72 | 59.29 | 0 | 0 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W06 | 2025-05-09 | 744 | 122 | 53389.6 | 722.18 | 21.82 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 97.07 | 0 | 100 | 58.82 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2025-06-10 | 720 | 122 | 48022.9 | 673.48 | 46.52 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 93.54 | 0 | 100 | 54.67 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2025-07-12 | 744 | 122 | 38740.7 | 544.6 | 199.4 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2 | 0 | 100 | 42.68 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2025-08-13 | 744 | 122 | 50695.9 | 695.2 | 48.8 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 93.44 | 0 | 100 | 55.85 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2025-09-14 | 720 | 122 | 24621.1 | 348.1 | 371.9 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 48.35 | 0 | 100 | 28.03 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2025-10-16 | 744 | 122 | 14730.1 | 202.83 | 474.6 | 677.43 | 82646.46 | 0 | 66.57 | 0 | 0 | 66.57 | 0 | 27.26 | 0 | 91.05 | 16.23 | 0 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 0 | 0
W06 | 2025-11-17 | 720 | 122 | 38218.5 | 529.83 | 190.17 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 73.59 | 0 | 100 | 43.51 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2024-12-19 | 744 | 122 | 53412.9 | 734.07 | 2.63 | 736.7 | 89877.4 | 0 | 0 | 0.43 | 6.87 | 7.3 | 6.87 | 98.67 | 0 | 99.02 | 58.85 | 0 | 0.0092339 | 3 | 0 | 0 | 0 | 0 | 1 | 0.43 | 1
W06 | Total | 8760 | 122 | 494258.3 | 6875.94 | 1794.32 | 8670.26 | 1057771.72 | 0 | 82.24 | 0.63 | 6.87 | 89.74 | 6.87 | 78.4342 | 0 | 98.995 | 46.1992 | 0 | 0.00076949 | 240 | 0 | 5 | 0.2 | 1 | 1 | 0.43 | 1
W07 | 2025-01-01 | 744 | 122 | 43388.3 | 613.62 | 130.38 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 82.48 | 0 | 100 | 47.8 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2025-02-02 | 672 | 122 | 34470.4 | 495.57 | 176.43 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 73.75 | 0 | 100 | 42.04 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2025-03-06 | 744 | 122 | 13539.6 | 200.42 | 185.85 | 386.27 | 47124.94 | 0 | 357.53 | 0.2 | 0 | 357.73 | 0 | 26.94 | 0 | 51.92 | 14.92 | 0 | 0 | 8 | 0 | 2 | 0.2 | 1 | 0 | 0 | 0
W07 | 2025-04-07 | 720 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W07 | 2025-05-09 | 744 | 122 | 6082 | 81.48 | 0 | 81.48 | 9940.56 | 0 | 662.52 | 0 | 0 | 662.52 | 0 | 10.95 | 0 | 10.95 | 6.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W07 | 2025-06-10 | 720 | 122 | 50018.6 | 702.32 | 17.68 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 97.54 | 0 | 100 | 56.94 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2025-07-12 | 744 | 122 | 46100.8 | 644.95 | 99.05 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 86.69 | 0 | 100 | 50.79 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2025-08-13 | 744 | 122 | 42708.8 | 587.53 | 156.47 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 78.97 | 0 | 100 | 47.05 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2025-09-14 | 720 | 122 | 23470.8 | 332.18 | 387.82 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 46.14 | 0 | 100 | 26.72 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2025-10-16 | 744 | 122 | 36060 | 506.9 | 179.83 | 686.73 | 83781.06 | 0 | 57.27 | 0 | 0 | 57.27 | 0 | 68.13 | 0 | 92.3 | 39.73 | 0 | 0 | 36 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W07 | 2025-11-17 | 720 | 122 | 37390.1 | 514.03 | 205.97 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 71.39 | 0 | 100 | 42.57 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2024-12-19 | 744 | 122 | 44979.6 | 618.38 | 118.32 | 736.7 | 89877.4 | 0 | 0 | 0.43 | 6.87 | 7.3 | 6.87 | 83.12 | 0 | 99.02 | 49.55 | 0 | 0.0092339 | 28 | 0 | 0 | 0 | 0 | 1 | 0.43 | 1
W07 | Total | 8760 | 122 | 378209 | 5297.38 | 1657.8 | 6955.18 | 848531.96 | 0 | 1797.32 | 0.63 | 6.87 | 1804.82 | 6.87 | 60.5083 | 0 | 79.5158 | 35.4008 | 0 | 0.00076949 | 241 | 0 | 5 | 0.2 | 1 | 1 | 0.43 | 1
W08 | 2025-01-01 | 744 | 122 | 41078.7 | 573.27 | 170.73 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 77.05 | 0 | 100 | 45.26 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-02-02 | 672 | 122 | 23904.1 | 345.3 | 326.7 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 51.38 | 0 | 100 | 29.16 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-03-06 | 744 | 122 | 32074.8 | 454.61 | 276.57 | 731.18 | 89203.96 | 0 | 12.62 | 0.2 | 0 | 12.82 | 0 | 61.1 | 0 | 98.28 | 35.34 | 0 | 0 | 23 | 0 | 2 | 0.2 | 1 | 0 | 0 | 0
W08 | 2025-04-07 | 720 | 122 | 53021.2 | 705.59 | 6.33 | 711.92 | 86854.24 | 0 | 8.08 | 0 | 0 | 8.08 | 0 | 98 | 0 | 98.88 | 60.36 | 0 | 0 | 14 | 0 | 2 | 0 | 0 | 0 | 0 | 0
W08 | 2025-05-09 | 744 | 122 | 55568.6 | 738.13 | 5.87 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.21 | 0 | 100 | 61.22 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-06-10 | 720 | 122 | 52102.7 | 714.38 | 5.62 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 99.22 | 0 | 100 | 59.32 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-07-12 | 744 | 122 | 52280.7 | 712.95 | 31.05 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 95.83 | 0 | 100 | 57.6 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-08-13 | 744 | 122 | 45755.5 | 619 | 125 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2 | 0 | 100 | 50.41 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-09-14 | 720 | 122 | 28854.4 | 396.08 | 323.92 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 55.01 | 0 | 100 | 32.85 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2025-10-16 | 744 | 122 | 35085.2 | 479.68 | 207.05 | 686.73 | 83781.06 | 0 | 57.27 | 0 | 0 | 57.27 | 0 | 64.47 | 0 | 92.3 | 38.65 | 0 | 0 | 30 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W08 | 2025-11-17 | 720 | 122 | 46020.3 | 627.87 | 92.13 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2 | 0 | 100 | 52.39 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2024-12-19 | 744 | 122 | 45359 | 612.63 | 124.07 | 736.7 | 89877.4 | 0 | 0 | 0.43 | 6.87 | 7.3 | 6.87 | 82.34 | 0 | 99.02 | 49.97 | 0 | 0.0092339 | 32 | 0 | 0 | 0 | 0 | 1 | 0.43 | 1
W08 | Total | 8760 | 122 | 511105.2 | 6979.49 | 1695.04 | 8674.53 | 1058292.66 | 0 | 77.97 | 0.63 | 6.87 | 85.47 | 6.87 | 79.5008 | 0 | 99.04 | 47.7108 | 0 | 0.00076949 | 242 | 0 | 5 | 0.2 | 1 | 1 | 0.43 | 1
W09 | 2025-01-01 | 744 | 122 | 40053.2 | 561.15 | 182.85 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 75.42 | 0 | 100 | 44.13 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-02-02 | 672 | 122 | 35146.5 | 504.35 | 167.65 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 75.05 | 0 | 100 | 42.87 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-03-06 | 744 | 122 | 34722.1 | 492.57 | 251.43 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 66.21 | 0 | 100 | 38.25 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-04-07 | 720 | 122 | 52414.3 | 703.23 | 13.87 | 717.1 | 87486.2 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 97.67 | 0 | 99.6 | 59.67 | 0 | 0 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W09 | 2025-05-09 | 744 | 122 | 55372.1 | 742.43 | 0.05 | 742.48 | 90582.56 | 1.52 | 0 | 0 | 0 | 1.52 | 1.52 | 99.79 | 0.2 | 99.8 | 61 | 0.2 | 0.002043 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-06-10 | 720 | 122 | 52022 | 720 | 0 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 59.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-07-12 | 744 | 122 | 54098.6 | 741.73 | 2.27 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.69 | 0 | 100 | 59.6 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-08-13 | 744 | 122 | 43346.6 | 586.3 | 157.7 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8 | 0 | 100 | 47.76 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-09-14 | 720 | 122 | 25429.5 | 357.66 | 360.07 | 717.73 | 87563.06 | 0 | 0 | 0 | 2.27 | 2.27 | 2.27 | 49.68 | 0 | 99.68 | 28.95 | 0 | 0.0031528 | 42 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W09 | 2025-10-16 | 744 | 122 | 39264.6 | 541.32 | 202.68 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 72.76 | 0 | 100 | 43.26 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2025-11-17 | 720 | 122 | 37672.8 | 514.8 | 175.87 | 690.67 | 84261.74 | 29.33 | 0 | 0 | 0 | 29.33 | 29.33 | 71.5 | 4.07 | 95.93 | 42.89 | 5.39 | 0.040736 | 25 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2024-12-19 | 744 | 122 | 47782.6 | 648.18 | 95.82 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 87.12 | 0 | 100 | 52.64 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | Total | 8760 | 122 | 517324.9 | 7113.72 | 1610.26 | 8723.98 | 1064325.56 | 30.85 | 2.9 | 0 | 2.27 | 36.02 | 33.12 | 81.1408 | 0.35583 | 99.5842 | 48.3533 | 0.46583 | 0.0038277 | 251 | 2 | 1 | 0 | 0 | 1 | 0 | 0
W10 | 2025-01-01 | 744 | 122 | 38977.2 | 538.42 | 205.58 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 72.37 | 0 | 100 | 42.94 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-02-02 | 672 | 122 | 35906.4 | 519.78 | 152.22 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 77.35 | 0 | 100 | 43.8 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-03-06 | 744 | 122 | 37647.5 | 535.87 | 204.93 | 740.8 | 90377.6 | 0 | 0 | 0 | 3.2 | 3.2 | 3.2 | 72.03 | 0 | 99.57 | 41.48 | 0 | 0.0043011 | 32 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W10 | 2025-04-07 | 720 | 122 | 53308.2 | 714.07 | 3.5 | 717.57 | 87543.54 | 0 | 2.43 | 0 | 0 | 2.43 | 0 | 99.18 | 0 | 99.66 | 60.69 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W10 | 2025-05-09 | 744 | 122 | 55623.4 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 61.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-06-10 | 720 | 122 | 52137.3 | 720 | 0 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 59.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-07-12 | 744 | 122 | 54341 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 59.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-08-13 | 744 | 122 | 43664.4 | 588.07 | 155.93 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 79.04 | 0 | 100 | 48.11 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-09-14 | 720 | 122 | 28940.5 | 400.95 | 319.05 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 55.69 | 0 | 100 | 32.95 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-10-16 | 744 | 122 | 42408.3 | 582.58 | 161.42 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3 | 0 | 100 | 46.72 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2025-11-17 | 720 | 122 | 42488.9 | 581.27 | 109.4 | 690.67 | 84261.74 | 29.33 | 0 | 0 | 0 | 29.33 | 29.33 | 80.73 | 4.07 | 95.93 | 48.37 | 4.8 | 0.040736 | 21 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2024-12-19 | 744 | 122 | 46672.1 | 628.47 | 115.53 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 84.47 | 0 | 100 | 51.42 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | Total | 8760 | 122 | 532115.2 | 7297.48 | 1427.56 | 8725.04 | 1064454.88 | 29.33 | 2.43 | 0 | 3.2 | 34.96 | 32.53 | 83.2633 | 0.33917 | 99.5967 | 49.7483 | 0.4 | 0.0037531 | 267 | 1 | 1 | 0 | 0 | 1 | 0 | 0
WAN | TOTAL | 87600 |  | 4324697.7 | 59636.58 | 23691.77 | 83328.35 | 10166058.7 | 94.9 | 3711.04 | 355.5 | 110.21 | 4271.65 | 205.11 | 68.0498 | 0.10842 | 95.1554 | 40.4661 | 0.12992 | 0.002331 | 2518 | 5 | 32 | 353.78 | 6 | 13 | 1.72 | 4
Total Project |  |  |  | 8415280 | [10 empty] | 65.5788 | 0.44229 | 89.6022 | 44.7973 | 0.50654 | 0.0060366
PR Availability Factor by Month |  |  |  | PR Forced Outage Factor |  |  | Percentage | YTD Percentage | FOER Hours | Accumulated Hours | Total Hours | YTD hours |  | PR | MWH per month | Available MWH |  | PR | Reserve Shutdown
| Actual | Required |  |  | Actual | Goal < 0.40
Jan | 90.651 | 86.52% |  | Jan | 0 | 0.4 | 0 | 0 | 0 | 7440 | 7440 | 0 |  | Jan | 391697.2 | 640722.75 |  | Jan | 155
Feb | 89.798 | 84.7% |  | Feb | 0.049 | 0.4 | 0.047701 | 0.023056 | 3.32 | 14400 | 6960 | 3.32 |  | Feb | 295966.7 | 573270.85 |  | Feb | 71
Mar | 80.39 | 77.85% |  | Mar | 0 | 0.4 | 0 | 0.015201 | 0 | 21840 | 7440 | 3.32 |  | Mar | 304896.4 | 568192.15 |  | Mar | 32
Apr | 71.97 | 76.43% |  | Apr | 7.925 | 0.4 | 7.9246 | 1.9762 | 570.57 | 29040 | 7200 | 573.89 |  | Apr | 378997.4 | 492270.05 |  | Apr | 41
May | 82.394 | 78% |  | May | 0.522 | 0.4 | 0.52218 | 1.6797 | 38.85 | 36480 | 7440 | 612.74 |  | May | 389167.8 | 582364.25 |  | May | 28
Jun | 89.683 | 89.6% |  | Jun | 0.248 | 0.4 | 0.2475 | 1.4436 | 17.82 | 43680 | 7200 | 630.56 |  | Jun | 366238.8 | 613434 |  | Jun | 145
Jul | 90 | 89.6% |  | Jul | 0 | 0.4 | 0 | 1.2335 | 0 | 51120 | 7440 | 630.56 |  | Jul | 289878.9 | 636120 |  | Jul | 197
Aug | 89.693 | 89.6% |  | Aug | 0.257 | 0.4 | 0.25699 | 1.1094 | 19.12 | 58560 | 7440 | 649.68 |  | Aug | 386157.1 | 633947.35 |  | Aug | 189
Sep | 77.807 | 77% |  | Sep | 0 | 0.4 | 0 | 0.98796 | 0 | 65760 | 7200 | 649.68 |  | Sep | 242068.2 | 532203.3 |  | Sep | 126
Oct | 70.449 | 67.03% |  | Oct | 0.273 | 0.4 | 0.27325 | 0.91531 | 20.33 | 73200 | 7440 | 670.01 |  | Oct | 281359.3 | 497932.05 |  | Oct | 160
Nov | 89.107 | 72% |  | Nov | 0 | 0.4 | 0 | 0.83335 | 0 | 80400 | 7200 | 670.01 |  | Nov | 351025.6 | 609497.2 |  | Nov | 186
Dec | 86.646 | 85.7% |  | Dec | 0.04 | 0.4 | 0.04086 | 0.76622 | 3.04 | 87840 | 7440 | 673.05 |  | Dec | 413128.9 | 612418.45 |  | Dec | 58
Wan Availability Factor by Month |  |  |  | Wan Forced Outage Factor |  |  |  | YTD Percentage | FOER Hours | Accumulated Hours | Total Hours | YTD hours |  | Wan | MWH per month | Available MWH |  | Wan | Reserve Shutdown
| Actual | Required |  |  | Actual | Goal < 0.40 | Percentage
Jan | 99.742 | 93.48% |  | Jan | 0 | 0.4 | 0 | 0 | 0 | 7440 | 7440 | 0 |  | Jan | 398655.5 | 905332.72 |  | Jan | 278
Feb | 100 | 95.3% |  | Feb | 0 | 0.4 | 0 | 0 | 0 | 14400 | 6960 | 0 |  | Feb | 297620.7 | 819840 |  | Feb | 199
Mar | 94.843 | 92.15% |  | Mar | 0 | 0.4 | 0 | 0 | 0 | 21840 | 7440 | 0 |  | Mar | 307468.1 | 860858.84 |  | Mar | 195
Apr | 89.307 | 87.57% |  | Apr | 0 | 0.4 | 0 | 0 | 0 | 29040 | 7200 | 0 |  | Apr | 408502.6 | 784456.34 |  | Apr | 240
May | 90.62 | 88% |  | May | 0.475 | 0.4 | 0.47567 | 0.097012 | 35.39 | 36480 | 7440 | 35.39 |  | May | 430585.4 | 822534.98 |  | May | 165
Jun | 100 | 99.6% |  | Jun | 0 | 0.4 | 0 | 0.081021 | 0 | 43680 | 7200 | 35.39 |  | Jun | 405115.6 | 878400 |  | Jun | 168
Jul | 100 | 99.6% |  | Jul | 0 | 0.4 | 0 | 0.069229 | 0 | 51120 | 7440 | 35.39 |  | Jul | 323454.8 | 907680 |  | Jul | 234
Aug | 100 | 99.6% |  | Aug | 0 | 0.4 | 0 | 0.060434 | 0 | 58560 | 7440 | 35.39 |  | Aug | 407401.9 | 907680 |  | Aug | 149
Sep | 94.625 | 89% |  | Sep | 0 | 0.4 | 0 | 0.053817 | 0 | 65760 | 7200 | 35.39 |  | Sep | 245634.8 | 831193.32 |  | Sep | 256
Oct | 84.812 | 72.97% |  | Oct | 0 | 0.4 | 0 | 0.048347 | 0 | 73200 | 7440 | 35.39 |  | Oct | 295655.3 | 769824.88 |  | Oct | 229
Nov | 93.606 | 78% |  | Nov | 0.826 | 0.4 | 0.82653 | 0.11803 | 59.51 | 80400 | 7200 | 94.9 |  | Nov | 381717.7 | 822226.32 |  | Nov | 179
Dec | 94.31 | 96.3% |  | Dec | 0 | 0.4 | 0 | 0.10804 | 0 | 87840 | 7440 | 94.9 |  | Dec | 422885.3 | 856031.3 |  | Dec | 226
Project Availability Factor by Month |  |  |  | Project Forced Outage Factor |  |  |  | YTD Percentage | FOER Hours | Accumulated Hours | Total Hours | YTD hours |  | Project | MWH per month | Available MWH
| Actual | Required |  |  | Actual | Goal < 0.40 | Percentage
Jan | 95.1965 | 90 |  | Jan | 0 | 0.4 | 0 | 0 | 0 | 14880 | 14880 | 0 |  | Jan | 790352.7 | 1546055.47
Feb | 94.899 | 90 |  | Feb | 0.0245 | 0.4 | 0.023851 | 0.011528 | 3.32 | 28800 | 13920 | 3.32 |  | Feb | 593587.4 | 1393110.85
Mar | 87.6165 | 85 |  | Mar | 0 | 0.4 | 0 | 0.0076007 | 0 | 43680 | 14880 | 3.32 |  | Mar | 612364.5 | 1429050.99
Apr | 80.6385 | 82 |  | Apr | 3.9625 | 0.4 | 3.9623 | 0.9881 | 570.57 | 58080 | 14400 | 573.89 |  | Apr | 787500 | 1276726.39
May | 86.507 | 83 |  | May | 0.4985 | 0.4 | 0.49892 | 0.88834 | 74.24 | 72960 | 14880 | 648.13 |  | May | 819753.2 | 1404899.23
Jun | 94.8415 | 94.6 |  | Jun | 0.124 | 0.4 | 0.12375 | 0.76231 | 17.82 | 87360 | 14400 | 665.95 |  | Jun | 771354.4 | 1491834
Jul | 95 | 94.6 |  | Jul | 0 | 0.4 | 0 | 0.65136 | 0 | 102240 | 14880 | 665.95 |  | Jul | 613333.7 | 1543800
Aug | 94.8465 | 94.6 |  | Aug | 0.1285 | 0.4 | 0.12849 | 0.58493 | 19.12 | 117120 | 14880 | 685.07 |  | Aug | 793559 | 1541627.35
Sep | 86.216 | 83 |  | Sep | 0 | 0.4 | 0 | 0.52089 | 0 | 131520 | 14400 | 685.07 |  | Sep | 487703 | 1363396.62
Oct | 77.6305 | 70 |  | Oct | 0.1365 | 0.4 | 0.13663 | 0.48183 | 20.33 | 146400 | 14880 | 705.4 |  | Oct | 577014.6 | 1267756.93
Nov | 91.3565 | 75 |  | Nov | 0.413 | 0.4 | 0.41326 | 0.47569 | 59.51 | 160800 | 14400 | 764.91 |  | Nov | 732743.3 | 1431723.52
Dec | 90.478 | 91 |  | Dec | 0.02 | 0.4 | 0.02043 | 0.43713 | 3.04 | 175680 | 14880 | 767.95 |  | Dec | 836014.2 | 1468449.75